| GENERAL SHOP INSPECTION |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SERVICE FACILITY: 26489 Industrial Blvd PHONE: 218-999-5100 Cohasset, MN 55721 |  |  |  |  |  |  |  |
| CUSTOMER: |  |  |  |
| SERVICE JOB: | Click or tap here to enter text. |  |  | SERVICE TECHNICIAN |  |  |  |
| INSPECTION DATE: | 1/19 THRU 1/22 |  |  | NAME: | DH |  |  |
| EQUIPMENT INFORMATION |  |  |  |  |  |  |  |
| MANUFACTURER: | GOULDS |  |  | EQ TYPE: |  | SPLIT CASE ROTATING ELEMENT |  |
| MODEL: | 3420LDS |  |  | SIZE: |  | 30X30-31 |  |
| SERIAL NUMBER: | BASED ON |  |  | IMPELLER TRIM: |  | 31-3/8” RIGHT HAND ROTATION |  |
| VISUAL INSPECTION NOTES: (BEFORE TEARDOWN) |  |  |  |  |  |  |  |
| - THIS ELEMENT HAS PREVIOUSLY BEEN WORKED ON, BUT HAS NO CRANE ENGINEERING TAGS ON IT |  |  |  |  |  |  |  |
| TEARDOWN INSPECTION NOTES: |  |  |  |  |  |  |  |
| - PRIOR TO DISASSEMBLY .027” OF END FLOAT WAS MEASURED - THE THRUST END BEARING HOUSING HAD BEEN SLEEVED AND A SHIM (APPROXIMATELY ¼” THICK) HAD BEEN ADDED TO THE HOUSING. - THE HOUSINGS HAD NO GASKETS, IN PLACE OF GASKETS RTV WAS USED. - BOTH BEARING HOUSING BORES WERE FOUND TO BE OVERSIZED. THE DRIVE END HOUSING MEASURED 9.846” WHILE THE OPPOSITE DRIVE END MEASURED 9.8542” - THE RADIAL END HOUSING HAS ONE BOLT HOLE THAT HAS BEEN HELICOILED, WHICH COULD BECOME AN OIL LEAK PATH - THE VANES ON BOTH SIDES OF THE IMPELLER HAVE SLIGHT WEAR - THE IMPELLER BORE IS WITHIN TOLERANCE, BUT IS AT THE TOP END - THE WEAR RINGS ARE WORN. THE CASING RINGS WILL NEED TO BE SKIM CUT TO BE MADE TRUE WHILE NEW IMPELLER RINGS WILL NEED TO BE MADE TO OEM CLEARANCES - THE SHAFT WAS FOUND TO BE STRAIGHT AND ALL LANDINGS ARE WITHIN TOLERANCES. THERE ARE SOME LIP SEAL GROOVES WORN INTO THE SHAFT THAT CAN BE CHROMED. - THE SHAFT WAS NDT TESTED AND NO DEFECTS WERE FOUND |  |  |  |  |  |  |  |
| RECOMMENDATIONS: |  |  |  |  |  |  |  |
| - REPLACE BEARING HOUSINGS, HOUSING COVERS, SLEEVES, SLEEVE NUTS, STUFFING BOX BUSHINGS, BEARINGS, INPRO LABYRINTH SEALS, AND MISC O-RINGS, GASKETS, AND HARDWARE - MACHINE LIP SEAL AREAS ON SHAFT, SKIM CUT CASING WEAR RINGS, CREATE NEW IMPELLER WEAR RINGS (FLASHED) - BALANCE ASSEMBLY TO G1.0 SPEC – COTTON BALL FINISH |  |  |  |  |  |  |  |
| INSPECTION TIME SPENT: |  | Inspect Hours | ESTIMATED REPAIR TIME NEEDED: |  |  |  |  |

| INSPECTION PICTURES |  |
| --- | --- |
| ROTATING ELEMENT WAS RECEIVED IN THE PICTURED CRATE | RADIAL END PRE-INSPECTION PHOTO |
| THRUST END PRE-INSPECTION PHOTO | IMPELLER VANE WEAR |

| INSPECTION PICTURES |  |
| --- | --- |
| IMPELLER VANE WEAR CONTINUED | SLEEVED BEARING HOUSING |
| DEBRIS FOUND IN RADIAL BEARING HOUSING | DEBRIS FOUND IN RADIAL BEARING HOUSING CONTINUED |

| INSPECTION PICTURES |  |
| --- | --- |
|  | INTENTIONALLY LEFT BLANK |
| SHAFT SLEEVE WEAR |  |
| INTENTIONALLY LEFT BLANK | INTENTIONALLY LEFT BLANK |